## Slide 1: A2.2: Concerted Actions on Energy Efficiency in Buildings TWG2: Building Renovation
Case Study: Promoting Energy Efficient Technologies through Good Practices in Public Buildings
March 29th, 2022
Mohammad Musleh, Energy Specialist, RSS/NERC Jordan

## Slide 2
Concerted Action on Buildings
29 March 2022
Overview
Case Study: Iskan Faiha' primary mixed School. (Public School)
Location: Madaba is located south-west of the capital Amman.
Project: “SOLE” High Energy efficiency for the pubLIc stOck buildingS in Mediterranean
Project Partners: Italy, Greece, Egypt, Jordan, Lebanon, Spain, Tunisia
Timeline: September 2021 – February 2022
Budget: 250,000 Euro

## Slide 3: Main Goals
Concerted Action on Buildings
29 March 2022
Support and encourage students and local community to use clean energy.
Enhance education environment and classrooms atmosphere.
Provide classrooms with required space heating and cooling in different seasons.
Reduce energy consumption of public schools and mitigate greenhouse gas emissions.
Disseminate the concept of energy and water management for students and the community.
Support and encourage students and local community to use clean energy.

## Slide 4
Concerted Action on Buildings
29 March 2022
Students Uncomfortable in cold weather

## Slide 5: Project Stages
Concerted Action on Buildings
29 March 2022
RSS/NERC performed stages 1 & 2 and supervised stage 3 as the implementation was carried out via local contractors
Stage 1
Energy Assessments, HVAC & PV Designs and Economic analysis
Stage 2
Measures Selection
Stage 3
Implementation via local contractors
Bidding

## Slide 6
Concerted Action on Buildings
29 March 2022
Main Figures
School Name | Land Area (m2) | No. of Buildings | No. of Classrooms | No. of Rooms | Number of Students | Working period
Location: North-West of Madaba |  |  |  |  |  | 
Iskan Faiha' primary mixed School | 2,930 | 1 | 30 | 41 | 725 | Morning

## Slide 7
Concerted Action on Buildings
29 March 2022
Main Findings
Energy Consumption/ Electrical System
Estimated annual Electric Energy Consumption (kWh) | Estimated annual Electric Energy Cost (JOD) | Average Electric Tariff (JOD/kWh)
30,000 | 3000 | 0.1
Chart: 
| Total Lighting | Total Equipment
 | 37.258 | 55.42
Total Connected Load proportion

## Slide 8
Concerted Action on Buildings
29 March 2022
Selected Energy Efficiency Measures
  Replacing Lighting Units
  Domestic hot water System
  Thermal insulation external walls and roofs, double glaze with PVC frame
  heating and cooling systems (AC split units)
Selected Renewable Energy Systems
  Domestic hot water System
  PV System (84 kWp)

## Slide 9
Concerted Action on Buildings
29 March 2022
Lighting system Retrofit
Replacing Lighting Units | No. of lamps | Connected load (Kw) | Annual Saving Cost (JOD)
Replace (Fluorescent tube 36w ) with (LED tube 18w) | 685 | 12.3 | 1315
Replace (CFL) with (LED round panel18W) | 60 | 1.1 | 58
Replace MH 250W with 50W | 6 | 0.3 | 90
Total |  | 13.7 | 1,463
Selected Energy Efficiency Measures

## Slide 10
Concerted Action on Buildings
29 March 2022
Installing thermal insulation for external walls and roofs, double glaze with PVC frame
Component | Saving measure
External walls | Installing Polystyrene insulation panels (5 cm thickness) with gypsum boards as a covering material
Roof | Installing Polystyrene insulation panels (5 cm thickness) with tiles as a covering material
Windows | Replacing the existing windows with double glaze with PVC frame
Selected Energy Efficiency Measures

## Slide 11
Concerted Action on Buildings
29 March 2022
Installing thermal insulation for external walls and roofs, double glaze with PVC frame
Selected Energy Efficiency Measures

## Slide 12
Concerted Action on Buildings
29 March 2022
Install Heating and cooling systems
Floor | GF | 1st | 2nd | Total | Expected annual consumption (Kwh/Year.)
Design cooling and heating capacities after implementing the saving measures of the building envelope (ton) | 24.5 | 30 | 20 | 74.5 | 107,127
Selected Energy Efficiency Measures

## Slide 13
Concerted Action on Buildings
29 March 2022
Domestic Solar hot water System
Item | Description
Solar Thermal System Capacity | 1400 Lit/Day
System Type | Glazed flat plate collector
Required Free Space | 50 m2
Renewable Energy Systems

## Slide 14
Concerted Action on Buildings
29 March 2022
Renewable Energy Systems Potential
Parameter | Value
System size | 84 kWp
System life expectancy | 20 years
Energy generation for the first year | 131,040 kWh
Annual system degradation | 1%
Average Tariff | 0.10 JD/kWh
First Year Saving cost (JD) | 13,104
Photovoltaic System

## Slide 15
Concerted Action on Buildings
29 March 2022
Renewable Energy Systems Potential
Chart: Current Energy Consumption Versus Generation Pattern
Yearly Energy Production (kWh) of 84 kWp | 131040 | 127108.8 | 125837.712 | 124579.3349 | 123333.5415 | 122100.2061 | 120879.2041 | 119670.412 | 118473.7079 | 117288.9708 | 116116.0811 | 114954.9203 | 113805.3711 | 112667.3174 | 111540.6442 | 110425.2378 | 109320.9854 | 108227.7755 | 107145.4978 | 106074.0428
Yearly Energy Consumption (kWh) | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901 | 112901
Photovoltaic System

## Slide 16
Concerted Action on Buildings
29 March 2022
Renewable Energy Systems
Photovoltaic System

## Slide 17
Concerted Action on Buildings
29 March 2022
Figures and Numbers
84 tons
CO2-equivalent emissions reduction per year

## Slide 18: Implementation Images
Concerted Action on Buildings
29 March 2022

## Slide 19: Implementation Images
Concerted Action on Buildings
29 March 2022

## Slide 20
Concerted Action on Buildings
29 March 2022
The Energy Globe Award for 2021
“Public Schools Heating Project”

## Slide 21
Concerted Action on Buildings
29 March 2022
Thanks
for your attention